## Sheet1
Discipline | Observation/Comments
Architecture | * Confirm pressurization of egress enclosures coordinated with MEP in salt-air conditions.
Architecture | * Specify 316 SS or HDG fasteners/anchors within marine exposure; avoid galvanic pairing.
Architecture | * Verify impact-resistant glazing or shutters per windborne debris region; DP ratings indicated.
Architecture | * Verify continuous air/water barrier at transitions (balcony-to-wall/roof-to-wall) with positive drainage.
Architecture | * Confirm roof overflow provisions and coastal-rated membranes and accessories.
Civil | * Locate meters, BFPs above DFE or floodproof; maintain access during flood events.
Civil | * Verify positive drainage and water quality treatment; pervious/impervious accounting.
Civil | * Coordinate MOT/ROW permits for off-site improvements.
Civil | * Confirm FFEs comply with DFE and municipal SLR policies.
Civil | Coastal/Resilience
Civil | Confirm the extent (sitework, utilities, etc.) of the current phase of the project
Civil | Confirm extents of off-site improvements
Civil | Confirm fence boundaries, as off site improvements require fence extension
Civil | Confirm loading dock manuevering requirements
Civil | Confirm access to grease traps from the street
Civil | Confirm fence and gate locations match Coastal logistics
Civil | Confirm connections between plumbing and civil
Civil | Confirm inverts of plumbing pipes with civil
Civil | Coordinate elevations from exteriors to interiors with architectural set
Civil | Coordinate hardscape and landscape with landscape set
Civil | Coordinate cranes, hoists, etc. with onsite utilities (drainage wells, grease traps, etc.)
Civil | Coordinate easements (if any)
Cover Sheet | * Verify Flood Zone, Base Flood Elevation (BFE), and Design Flood Elevation (DFE) on cover; confirm datum (NAVD88) and map source/date.
Cover Sheet | * Confirm Risk Category, Basic Wind Speed (ASCE 7-22), Exposure Category, and windborne debris designation (HVHZ where applicable).
Cover Sheet | * List Threshold Inspector and Geotechnical Engineer when required.
Cover Sheet | * Confirm code editions and local amendments.
Electrical | * Elevate switchgear/panels/generators above DFE; NEMA 3R/4X outdoors.
Electrical | * Fuel storage, ventilation, exhaust, flood protection verified.
Electrical | * Coastal/UV-rated luminaires and hardware; turtle-friendly where applicable.
Electrical | * Coordinate survivability pathways and elevations for low-voltage and FA.
Electrical | Confirm required lumens are being met (10 lumens required at elevator openings)
Electrical | Confirm what is connected to emergency generators with owner/architect
Electrical | Confirm egress lighting requirements are being met at amenities
Electrical | Confirm wire type - all copper preferred, copper and aluminum acceptable
Electrical | Provide EV charging in garage (5% for TCO, infrastructure for 20%)
Electrical | Hard pipe required for conduits passing through waterproofing or roofing
Electrical | Confirm conduit is properly spaced if penetrating exterior location to allow for waterproofing/roofing. Minimum spacing of 2" between conduit is required at these locations
Electrical | Confirm conduit runs/power
Electrical | Parking garage security system
Electrical | Outdoor kitchens
Electrical | Cabanas (if needed)
Electrical | Pool lighting
Electrical | Coordinate concrete encased conduit with structure
Electrical | Consider proximity of main electrical room/switch gear to FPL vault (preferred abutting or stacked)
Electrical | FPL vault typically required to be 30'0" by 30'0" (to be confirmed with FPL)
Electrical | Consider location of FPL vault with phasing of construction
Electrical | Consider required street access of FPL vault
Electrical | Confirm height clearance of FPL vault and switch gear room (12'0" required)
Electrical | Consider location of external FPL lines coming into site for location of temp power and FPL vault
Electrical | Coordinate with architectural set about outlets in columns
Electrical | Confirm 12'0" required distance between outlets
Fire Protection | * Use corrosion-resistant sprinklers/piping; consider MIC mitigation.
Fire Protection | * Elevate/protect fire pump & riser rooms above DFE; provide ventilation/drainage.
Fire Protection | * Verify FDC, hydrants, and access with Civil and AHJ.
Fire Protection | Specify where fire stair drain will be connected to (coordinate with plumbing)
Fire Protection | Confirm if more sprinklers will be needed at EV chargers based on feedback from the City of Miami
Fire Protection | Avoid penetrating link beams and sleeve sprinklers through shear wall
Fire Protection | Confirm no obstacles in clear egress path such as control valves
Fire Protection | Confirm whether fire sprinklers are needed at balconies (typically needed if enclosed on 3 sides and depth exceeds 4'0", over an occupied space)
Fire Protection | Confirm wall assemblies include complete backup for all UL, ASTM, STC, or other reference
Fire Protection | Confirm all fire rated assemblies are 100% compliant
Fire Protection | Confirm stud spacing is in compliance with required board laps for UL assembly and STC ratings
Fire Protection | All penetrations contained within/passing through fire rated assemblies must meet the requirements of the assemblies
Fire Protection | Confirm that thinwall/lightwall black or galvanized pipe are not used. These pipes will be subsituted with EOR approved grade Schedule 10 or Schedule 40
Fire Protection | Confirm fire proofing is compatible with CPVC (If CPVC is specified)
Fire Protection | Confirm fire proofing is rated Type W for water resistance (if CPVC is not specified)
Fire Protection | Clothes closets, linen closets and pantries not exceeding 24 square feet (2.2 m2) in area, with the smallest dimension not greater than 3 feet (915 mm) and having wall and ceiling surfaces of gypsum board.
Fire Protection | Bathrooms not more than 55 square feet (5.1 m2) in area.
Interior Design | * Use moisture/salt-air tolerant finishes near openings and semi-conditioned spaces.
Interior Design | * Specify marine-grade hardware/finishes for exterior-adjacent FF&E.
Interior Design | Provide information on built-in furniture
Interior Design | Define floor finish and dimension of materials
Interior Design | Based on floor finish, confirm slab elevation/recesses needed/accounted for
Interior Design | Confirm artificial or living planting of interior spaces (irrigation and drainage needed)
Interior Design | Consider materials at high traffic wet areas (wood is not desirable)
Interior Design | Confirm schedule and material tags match
Interior Design | Confirm coordination of lighting and power with electrical drawings
Interior Design | Confirm coordination of mechanical with mechanical drawings
Interior Design | Coordinate ceiling heights with MEP and structure
Interior Design | Confirm bathroom accessories are compliant with ADA and FHA
Interior Design | Confirm soffit depths and built in furniture will not cause fire sprinklers to be added
Interior Design | Metal panels should have a class "A" building material rating when tested in accordance with ASTM E84 (Steiner Tunnel Test), and exhibit a flame spread of less than 25, and smoke index of less than 450
Interior Design | Confirm all paint products comply and applied following AAMA (American Architectural Manufacturers Association) standard #2605. Must be 70% fluoropolymer resin-based coating
Interior Design | Confirm tile/stone cladded sink substructure is properly documented
Interior Design | Consider detail of wet room/shower located next to window wall system
Interior Design | Consider noise of BOH rooms, amenity spaces, etc next to quiet areas (library/coworking space)
Interior Design | Confirm steam shower ceiling is durock and has a transom air gap
Landscape | * Select salt/erosion-tolerant species; protect dunes/mangroves as applicable.
Landscape | * Non-corrosive materials; avoid overspray on envelope; proper backflow.
Landscape | * Marine-grade finishes; anchorages for wind uplift.
Landscape | Consider site landscape that may get damaged in future phases
Landscape | Confirm tree protection/mitigation plan is coordinated with Coastal logistics plan
Landscape | Coordinate artificial turf assembly (if any) with architecture
Landscape | Confirm landscaping layout matches architecture
Landscape | Coordinate landscape concrete curbs needed for tree anchoring with architecture and structure
Landscape | Coordinate cabana curbs with structure and arch
Landscape | Coordinate where structure fill is located on all drawings
Landscape | Confirm if silva cell/structural soil is needed (at ground level)
Landscape | Confirm if planter depth is enough for root ball specified
Landscape | Coordinate planter drains with plumbing
Landscape | Coordinate soil depths at elevated slabs with structural
Landscape | Coordinate water features with plumbing
Landscape | Coordinate irrigation with plumbing
Landscape | Confirm if planting is artificial or living (coordinate irrigation and drainage)
Landscape | Coordinate amenity deck features (cabanas,etc.) with MEP requirements (power, lighting)
Mechanical | * Place equipment above DFE; if not, provide barriers/dry floodproofing and service access.
Mechanical | * Garage ventilation (natural vs mechanical), CO monitoring, and intake/exhaust placement.
Mechanical | * Bathroom ventilation supply/return balance; corrosion-resistant ductwork near coast.
Mechanical | * Coastal-rated coils/fasteners; protective coatings for outdoor units.
Mechanical | * Service clearances, wash-down access, condensate management.
Mechanical | Confirm coordination of shear wall penetrations/sleeves (coordinate with structure)
Mechanical | Bathroom and dryer ducts that are exhausted at an exterior wall will be thermally insulated a minimum of 6' from the exterior wall. Ducts should be sloped downwards to prevent water from entering
Mechanical | Coordinate window washing/BMU systems with mechanical equipment on roof
Mechanical | Confirm coordination with Life Safety consultant on report/rational analysis
Mechanical | Consider providing AC vents to bathrooms
Mechanical | Confirm location of mechanical equipment is indoors and mechanically ventilated/air conditioned
Mechanical | Confirm if garage is required to be mechanically ventilated (coordinate with architecture)
Mechanical | Coordinate louvers needed with architectural elevations
Mechanical | Consider standardizing louvers (sizing and material)
Mechanical | Confirm louvers are directed downwards to prevent water infiltration
Mechanical | Coordinate location of housekeeping pads needed with structure
Mechanical | Consider horizontal exhaust in lieu of vertical (concern for water/moisture mitigation)
Mechanical | Confirm required 3'0" distance between exhaust vents and window openings/doors
Mechanical | Coordinate location of soffit exhaust at residential units with sliding door openings
Mechanical | Consider combining exhaust to 1 xvent (maximum 3)
Mechanical | Consider combining toilet exhausts to one 6" vent to minimize soffits
Mechanical | Consider location of generator exhaust and intake (prevailing winds)
Plumbing | * Provide secondary/overflow drainage; corrosion-resistant piping & fittings.
Plumbing | * Lift stations/ejectors above DFE or protected; N+1 where required.
Plumbing | * Dielectric isolation and corrosion-resistant materials in coastal zones.
Plumbing | Coordinate pool equipment room routing to pool
Plumbing | All wiring and equipment comply with NFPA
Plumbing | Confirm no smurf piping in wet areas
Plumbing | Confirm shower niches do not intersect water lines
Plumbing | Coordinate locations of sump pumps at basement and elevators
Plumbing | Confirm insulation is shown if PVC is specified
Plumbing | Confirm plumbing pipes and insulation fit within the specified drywall
Plumbing | Coordinate underground piping with structure
Plumbing | Confirm ground floor plumbing connections with civil
Plumbing | Back to back/mirror bathrooms where possible
Plumbing | Confirm underground PVC pipes have a trench width of the pipe's outside diameter plus 16 inches, or the pipe's outside diameter times 1.25, plus 12 inches. This trench will have backfill and bedding to support the pipe
Plumbing | Confirm all PVC pipes are supported every 4 ft